## Use cases
Paper | Definition of DER/MG/SG | Background & overview | Microgrid configuration |  |  |  | Design intent |  |  | Conceptual framework | Implementation framework | Technology |  | Study/scenario | Result | Challenge | Limitation | Conclusion
|  |  | Deployment context | DER composition | Topology | Operating mode (islanded/grid-connected) | DT purpose | Data analytics type (descriptive/predictive/prescriptive) | User |  |  | DT side | MG side
2 | A microgrid is described as self-sufficient, localised grids that seamlessly integrate diverse distributed energy resources, including renewables, energy storage, and advanced control systems, fostering both resilience and sustainability. | The case focuses on the Singapore Institute of Technology (SIT) @ NYP campus. Researchers modeled the campus microgrid for real-time simulation, using load demand and weather data collected from the site. The system of interest is the HVAC cooling system with chillers, cooling towers, pumps, AHUs, and FCUs | Building | Solar PV, BESS | Single | Both. • Grid-connected mode - interacts with the main utility grid but with constraints (e.g., no power export back to the main grid, maximum infeed 200 kW) • Islanded mode - can operate independently in case of grid outage, supported by a backup combined heat and power (CHP) unit for reliability | 1. Examine how the microgrid responds to variable PV generation and fluctuating load demand. 2. Support energy cost reduction and grid stability by generating optimised control strategies 3. Provide predictive insights and optimised operational profiles for building operators, reducing reliance on manual interventions | All | Building operator | Integrates: 1. Forecasting layer -> predicts building HVAC load demand using historical & weather data. 2. Optimisation layer -> determines optimal BESS dispatch based on load forecast and PV generation 3. Digital Twin layer -> simulates the microgrid in real time | Four components: 1. Siemens Microgrid Controller (MGC) - Central control unit for both physical and virtual systems - Executes same logic in DT and real grid for fidelity - Manages energy flow, storage and DER coordination - Sends real-time setpoints 2. Engineering PC - Human-machine interface for monitoring, configuration and control - Hosts supervisory tools and simulation environments - Bridges human input with DT execution 3. Real-time Simulator (OPAL RT 5700) - Runs real-time simulation of the microgrid (DERs, loads, topology) - Supports Hardware-in-the-Loop (HIL) for synchronous interaction with physical devices - Models dynamic/transient grid behavior for predictive control 4. Toolbox Server - Provides extra computing power for simulation, forecasting and optimisation - Hosts solvers (e.g., Gurobi) and AI models - Enables advanced analytics and parallel computation The components communicate seamlessly over the IEC 60870-104 protocol, which is a standardised network protocol commonly used in power system controls. This ensures accurate, secure, and timely exchange of measurements, control commands, and state variables required for real-time coordination. | 1. LSTM neural network -> forecasting/prediction 2. Gurobi -> optimisation (cost minmisation & variance reduction in BESS scheduling) | 1. OPAL-RT RT-Lab with Matlab -> for simulation 2. Siemens Microgrid Controller (MGC A8050) 3. IEC 60870-5-104 communication protocol | 2 types of optimisation objectives: Scenario 1: minimise cost • goal: to reduce total daily building electricity cost • variants: - 1A (fixed SOC): battery starts the day with fixed 50% charge - 1B (flexible SOC): battery's starting SOC can be optimised for flexibility Scenario 2: minimise variance • goal: to stabilise the grid infeed power by minimising fluctuations • rationale: high peaks/valleys in power demand stress the main grid, requiring extra infrastructure and cost. Reducing variance improves grid stability and efficiency. | Scenario 1A: • Predicted and actual BESS control profiles matched closely. • Reduced building energy cost from SGD 1334 → 1028 (≈ 23% savings). Scenario 1B: • Further improved optimisation flexibility. • Reduced cost to ~SGD 1017, saving SGD 317 compared to no DT optimisation. • Showed that allowing DT to optimise initial battery charge gave better outcomes. Scenario 2: • Reduced fluctuations in grid power demand, making the microgrid’s interaction with the main grid smoother and less resource-intensive. • While cost savings were less than Scenario 1, this scenario emphasised grid reliability. Prediction model: • The one-layer LSTM with Standard scaler provided the best balance of accuracy and simplicity • More complex two-layer LSTM tends to overfit, especially with limited training data | • Scale mismatch between the experimental microgrid and NYP building requires adjustment • Complexity in integrating MGC logic to provide maximum accuracy in the DT • Real-time fidelity requirement • Unavoidable power losses across conversion, transmission, and auxiliary devices affecting real-world performance. | • DT has to be tested under multiple conditions (islanded vs grid-connected, dynamic vs steady-state, component vs system level) to ensure fidelity, but these are not included in the paper due to page limitation • Forecasting depends on training data quality/availability • Non-HVAC loads modeled simplistically; full building diversity not captured. | • The DT showed high fidelity, with simulation results closely matching the physical microgrid’s performance • Demonstrates benefits: 23% cost reduction for building operations and improved grid stability • Highlights the potential of DTs as decision support and predictive control tools for campus buildings
3 | Microgrid is a small power system composed of distributed power resources, energy storage systems, loads, monitoring and protection devices, and other equipment. Usually composed of multiple DERs. DERs are distributed energy resouces such as solar panels, wind turbines etc. | The paper examines a smart microgrid consisting of wind, solar and energy storage systems. Microgrids face diverse and frequent risks compared to traditional grids, due to distributed generation and complex device interactions . To address these challenges, the authors propose a digital twin-enhanced Opportunistic Maintenance framework and validate it through a numerical case study of a wind-solar-storage microgrid with 17 major devices. | Consists of 17 major devices (PV units, wind units, diesel units, batteries, converters, circuit breakers, etc.) | solar, wind, diesel with energy storage | Single | Islanded | • Enable real-time monitoring of device conditions. • Support intelligent simulation and visualisation of the microgrid’s operation state. • Guide Opportunistic Maintenance (OM) decisions, prioritising critical components when resources are limited . | All | Manager and O&M operators | Four-layer architecture: 1. Perception layer -> contains sensors & data acquisition devices to monitor equipment, environment, operations and maintenance data 2. Data layer -> manages the collected data and transforms it into DT data 3. Model layer -> core of the DT microgrid, providing a real-time mirror model of the microgrid using real-time & historical data; guide preventive & targeted operation and maintenance decisions 4. Application layer -> optimise the DT model of the microgrid with the actual operation through visualisation and interactive functions (e.g. emergency response, operational optimisation, load scheduling) for the managers, achieving closed-loop feedback | Components of implementation: 1. Virtualisation of physical entities - Creates real-time, dynamic virtual replicas of key microgrid components: generators, inverters, energy storage, environmental systems, and even operators. - Models system states, behaviors, and interactions accurately. 2. Real-time data acquisition & integration - Uses sensors to collect real-time data on equipment condition, environment, and operations. - Synchronises virtual and physical systems via continuous data streaming. 3. Intelligent simulation & analysis - Simulates operational scenarios using both real-time and historical data. - Performs Fault Tree Analysis and dynamic risk assessments to predict failures & vulnerabilities. 4. Monitoring & maintenance decision support - Offers real-time visualisation of equipment and system health. - Enables predictive maintenance (corrective, preventive, opportunistic) based on real-time risk assessment. - Optimises scheduling by considering cost, resource constraints and device interdependencies. 5. Feedback & closed-loop control - Maintenance schedules and control decisions from the DT are sent back to the physical system for execution. - Results from the operations (post-maintenance states, updated data) is fed back into the DT, enabling continuous refinement. 6. Risk importance & correlation analysis - Assesses each device’s impact on system risk using a Risk Importance Measure. - Groups devices into correlation sets for coordinated maintenance, minimising downtime and maximising resource efficiency. | • Modeling layer -> Fault Tree Analysis (FTA) for system failure analysis. • Optimisation & decision-making: Risk Importance Measure to prioritise devices for OM under resource constraints. | 1. DC/DC, DC/AC converters 2. Filters, circuit breakers 3. Intelligent Energy Management (IEM) 4. Sensors & data switch | The experiment applies the DT-based maintenance model to a wind-solar-storage microgrid with 17 devices. Three scenarios are tested: • Scenario 1: Only corrective maintenance (CM). • Scenario 2: Preventive maintenance (PM) with fixed thresholds, but no OM. • Scenario 3 (proposed): Combines CM, PM, and DT-enabled OM with correlation sets and risk importance measure. | • Scenario 1: 172 shutdowns, total cost ≈ 5.29M, average reliability = 0.56. • Scenario 2: 265 shutdowns, total cost ≈ 6.14M, average reliability = 0.93. • Scenario 3 (DT-enhanced OM): 128 shutdowns, total cost ≈ 3.52M, average reliability = 0.97. | • Data integration across heterogeneous sources (sensors, UAVs, cameras) into standardised DT format. • Real-time reliability assessment and dynamic correlation set updates demand high computational performance. • Complexity of fault propagation modeling in multi-device microgrids makes building accurate DT models challenging. • DT effectiveness relies on reliable sensor data transmission, which can be prone to failure. | • Maintenance thresholds assumed or randomly generated, which may not fully reflect real device behavior. • Future work: handling high-dimensional, multi-source data and improving reliability of sensor data transmission. | DT provides a systematic, data-driven approach for optimising maintenance in complex microgrids, but further work is needed on real-world data integration and robustness.
11 | No definition, but states that it includes "photovoltaic panels (PVs), small-scale wind turbines, batteries for energy storage, and biomass generators" | • The paper addresses the challenges of integrating (DERs) (i.e. PV, EVs, batteries) into residential distribution grids. • Increasing DER adoption transforms consumers into prosumers, adding complexity and stressing distribution systems. • The framework is validated using two Danish residential grids as case studies, simulating DER adoption over 15 years. | Residential | EV, PV, BESS | Interconnected | Both | • The DT framework aims to give visibility, simulation, and decision-support for DSOs (distribution system operators). • Helps anticipate grid impacts of high DER adoption (overloads, voltage issues). • Provides a virtual environment to test grid reinforcements, consumer behavior, and energy policies. | Descriptive, Predictive | DSO, policymakers | Four core modules & 12 agents: • DER module -> EV, roof PVs, stationary battery • Electricity distribution module -> distribution grid, cable box, consumer connection point, cable, transformer • Energy Management System module -> EMS, control strategy • Electricity consumer module -> residential consumer, base appliances | DERInGrid simulation framework, built on agent-based simulation (ABS). ABS models the electricity system as a collection of distinct agents, each with defined roles, states, behaviors, and interaction protocols. Agents are designed to represent different real-world entities and devices in the grid ecosystem. Agent Behavior and Communication • DER agents, such as EVs, PVs, and Batteries, have detailed statecharts and logic mimicking real behaviors: - EV agents cycle through states (Idle, Driving, Connected_to_Charger, Charging) driven by trip scheduling and energy consumption/charging. - PV agents generate DC power proportional to solar irradiance, connected to inverters converting DC to AC. - Battery agents have charging/discharging states controlled by the EMS, considering state-of-charge (SoC), depth-of-discharge (DoD), efficiencies and maximum rates. • Electricity distribution grid agents maintain power flow states, propagate load/generation changes upward through the radial network to a top-level transformer and monitor overload conditions. • EMS agents control DERs based on simple strategies like zero net flow or average load buffering, sending command signals to DER agents and adjusting power flows accordingly. • Residential Consumer agents manage adoption of DERs over time using logistic growth functions and assign schedules for EV trips. Data and Control Flow • DER agents exchange electrical power and status updates through interface-based communication protocols aligned with their roles and connections. • Power flow changes at consumer connection points are propagated upward through Cable Boxes, Cables, and Transformers to reflect real distribution grid behavior. • The EMS module communicates with DER agents to coordinate flexible charging/discharging per control strategies, considering observed net power flows. | AnyLogic 8.8.3 platform for ABS (agent-based simulation) | N/A | DERInGrid framework applied to two Danish grids: • Case 1: older district, 126 households, low initial DER but high adoption potential. • Case 2: newer district, 160 households, already includes PV installations. Three simulation scenarios over 15 years with DER adoption: • S.1 PV only: gradual adoption of rooftop PVs. • S.2 Batteries/EVs: stationary batteries (S.2A) and EVs (S.2B) • S.3 PV + Battery: combined adoption with Zero Net Flow EMS strategy to minimise grid export/import at consumer nodes. | Case 1: • PV adoption (S.1): creates midday export peaks since PV production exceeded consumption. • EV adoption (S.2B): causes strong evening load peaks due to synchronised charging (when residents return home). • Household batteries (S.2A) & PV+battery (S.3): effective in buffering both peaks & valleys, by absorbing midday PV surplus & discharging during evening EV charging. • Overall: Case 1 showed higher sensitivity to DER adoption, meaning problems like overloads appear sooner compared to Case 2. Case 2: • PV adoption (S.1): less dramatic export peaks compared to Case 1 because some PV smoothing is already present. • EV adoption (S.2B): still causes problems, but the grid handles it better due to more robust infrastructure. • Household batteries (S.2A) & PV+battery (S.3): improves grid balance but the marginal benefit was less than in Case 1 (because Case 2’s grid is more resilient already). • Overall: Case 2 demonstrated that newer grids are more DER-ready, and battery adoption is helpful but less critical. • PV-only adoption increases self-sufficiency but risks overvoltage and reverse power flow. • EV adoption causes sharp, synchronised demand spikes, stressing the grid. • Batteries provides the most significant stabilisation benefit across all scenarios. • The Zero Net Flow strategy in S.3 is especially effective, as it smooths net loads at consumer connection points, benefiting both the household and the grid. | • Integration of diverse DER technologies into one coherent model. • Balancing model abstraction vs detail in agent design (too simple -> inaccurate; too complex -> heavy computation). | • Case studies limited to two Danish grids, may not generalise globally. • Focuses only on residential sector (excludes commercial/industrial loads). • Future work: expand control strategies, add more grid detail extend to larger/more diverse systems. | • The DERInGrid DT framework is effective in simulating complex DER-grid interactions. • Provides DSOs and policymakers with a tool for planning grid reinforcements and energy policies. • Demonstrates value of agent-based DT for scalability and adaptability.
Y.1 | No definition of MG. EcoMicrogrid is an EMS tool, acting as the control and management system for microgrids, optimising their operation by coordinating energy generation, storage and consumption. It ensures efficient resource utilisation, minimises costs and enhances the overall performance of the microgrid. In essence, ecoMG is a specialised software solution that enables regular microgrids to operate more intelligently and effectively | • This paper focuses on evaluating the performance of the ecoMG tool, an Energy Management System (EMS) designed for microgrids and small off-grid systems. • It introduces an advanced Hardware-in-the-Loop (HIL) testing setup integrated with Real-Time Digital Twin (RTDT) technology to validate the tool's capabilities under realistic conditions. • The paper uses the Gaidouromandra microgrid in Greece as a case study, leveraging real-time data and a digital twin to simulate the microgrid's behavior. The ecoMG tool is tested for its ability to optimise energy management, reduce operational costs, and enhance system efficiency. Key functionalities such as load scheduling, renewable energy forecasting, and diesel generator control are evaluated through specific operational scenarios. | 14 vacation houses | • generation: 6 PV arrays • backup: 1 diesel generator • storage: BESS | single | islanded | • accurately emulate the real equipment installed at the Gaidouromandra site • validate the performance of the ecoMG • optimise ecoMG performance by enhancing its energy utilisation, minimise costs and improve reliability | Descriptive, Predictive | Researcher, engineer, ecoMG developer | N/A | 1. Digital Twin Model Development • Electromagnetic Transient (EMT) System: The DT is designed as a high-precision EMT model to emulate the physical microgrid system at the Gaidouromandra site. • Components: Includes battery storage dynamics, diesel generators (DG), power electronics interfaces (PELs), PV systems, household loads and HVAC systems. Thermal dynamics and environmental factors (e.g., solar exposure) are also incorporated. • Real-Time Digital Simulator (RTDS): The DT is implemented using RTDS hardware, specifically the NovaCor processing core and GTNETx2 network interface card, to achieve real-time operation. 2. Communication and Data Acquisition • Real-Time Automation Controller (RTAC): Functions as the central communication hub at the physical microgrid site, collecting data from microgrid assets and smart meters. • MQTT Protocol: Used for transmitting real-time data from the physical microgrid to the DT. • Modbus TCP Commands: The data acquisition service converts MQTT data into Modbus TCP commands for integration with the DT. • Bidirectional Communication: The ecoMG tool exchanges data and control commands with the DT via Modbus TCP, enabling real-time feedback and interaction. 3. Integration with ecoMicrogrid (ecoMG) Tool • Data Concentrator: Collects real-time data from the DT and physical microgrid, processes it, and stores it for use by the ecoMG tool. • High-Level Functions: Modules within the ecoMG tool (e.g., EMS, Forecast, DSM) interact with the DT to optimise MG operations and test control strategies. 4. Testing and Validation • Three-Phase Approach: Phase 1: Comprehensive modeling of the microgrid system in RSCAD, including electrical network topology, thermal dynamics, and control logic. Phase 2: Open-loop validation of the DT model to verify accuracy against physical microgrid measurements. Phase 3: Closed-loop HIL testing with the ecoMG tool as the Hardware Under Test (HUT). • Operational Scenarios: The DT is used to simulate specific scenarios (e.g., normal operation, high-load conditions) to evaluate the ecoMG tool's performance. 5. Real-Time Feedback and Control • The DT dynamically adjusts its simulation based on real-time data and control setpoints provided by the ecoMG tool, ensuring accurate replication of microgrid behaviour. • The ecoMG tool uses the DT to optimise energy management strategies, such as HVAC usage, PV curtailment and diesel generator operation. 6. Performance Evaluation • The DT enables detailed analysis of the ecoMG tool's impact on microgrid efficiency, operational costs and resource utilisation under various conditions. • Results from the DT simulations are compared with physical measurements to validate the tool's effectiveness. | • Electromagnetic Transient (EMT) Modeling: High-precision modeling of the microgrid system to replicate physical equipment and dynamics. • Real-Time Digital Simulator (RTDS): for real-time simulation of the microgrid. Key components include: NovaCor Processing Core: Provides advanced parallel processing for real-time operation. GTNETx2 Network Interface Card: Facilitates communication between the RTDS and external systems. • Data Acquisition Service: Converts MQTT data into Modbus TCP commands for integration with the DT • RSCAD Software: for detailed microgrid system modeling, including power electronic converters, diesel generators, loads and BESS. • SCADA Human-Machine Interface (HMI): Provides real-time visualisation of the microgrid's single-line diagram and operational data. Industrial Relays: Protect low-voltage feeders and monitor electrical lines | • MQTT Protocol: for real-time data transmission from the physical microgrid to the DT • Modbus TCP Protocol: Enables bidirectional communication between the ecoMG tool and the DT for data exchange and control commands. • Fiber Optic Communication Network: Provides high-speed (1 Gbps) connectivity for reliable data transmission within the microgrid. • Real-Time Automation Controller (RTAC): Serves as the central communication hub, collecting data from microgrid assets and smart meters. • ecoMG Tool: Incorporates advanced optimisation algorithms based on model predictive control techniques for energy management. Key modules include: Forecast Module: Uses meteorological and historical data for renewable energy and load predictions. Demand Side Management (DSM) Module: Enables load scheduling and dynamic pricing strategies. EMS Module: Implements control algorithms to optimise microgrid performance. • Mini PC for ecoMG Tool, with Server OS for running ecoMG services. • Smart Meters: Advanced meters for energy consumption monitoring and load control. | Scenario 1: Pre-Cooling strategy using surplus PV power • Objective: Demonstrate the ecoMG tool's ability to utilise surplus photovoltaic (PV) power during the day to pre-cool the control room, reducing HVAC usage at night and optimising energy consumption. • Conditions: - Initial battery State of Charge (SoC): 90%. - Room temperature limits: Upper limit of 30°C and lower limit of 25°C. • Key Actions: - The EMS activates the HVAC system during periods of curtailed PV production to maintain room temperature near the lower limit. - Proactive cooling reduces nighttime battery drain and alleviates daytime renewable energy curtailment. Scenario 2: Diesel generator optimisation under high load • Objective: Evaluate the ecoMG tool's ability to optimise diesel generator usage during peak load conditions, reducing operational time and fuel costs. • Conditions: - Initial battery SoC: 70%. - Actual load from the microgrid is doubled to simulate increased demand. • Key Actions: - The EMS predicts SoC drop due to nighttime demand and activates the diesel generator only when necessary (SoC reaches 40%). - The generator runs for 45 minutes to increase SoC by 5-6%, then shuts down when the EMS determines the SoC is adequate. | Scenario 1 • Battery charging is maintained above 90% SoC. • PV generation curtailment is reduced by utilising HVAC power during the day. • Nighttime battery discharge is minimised, improving overall energy efficiency. Scenario 2 • Diesel generator usage is reduced by 37.5% compared to traditional control methods. • Batteries remain within operational limits, avoiding excessive discharge. • Operational costs are significantly lowered while maintaining system reliability. | • high complexity of HIL + DT setup • The microgrid assets and communication infrastructure use different protocols (MQTT for data collection and Modbus TCP for interfacing with the DT model) -> interoperability challenge | • only 2 scenarios are evaluated • focuses solely on ecoMG | The DT implementation in the Gaidouromandra case study successfully replicated the physical microgrid using real-time data and advanced simulation models. It enabled robust testing and validation of the ecoMG Energy Management System under realistic conditions. The DT accurately emulated equipment dynamics, environmental factors and operational scenarios, facilitating optimisation of energy management strategies, such as reducing diesel generator usage, minimising renewable energy curtailments and improving HVAC efficiency
Y.2 | Microgrid(MG) is a small-scale power system that combines multiple sources of energy such as solar, wind, and/or conventional sources | This study focuses on energy management in microgrids (MGs) with high penetration of renewables. It addresses challenges of stochastic load variation, energy flow and distribution network limitations. Case study applies DT to integrate PV, wind, diesel generators, and batteries. | N/A | Solar PV, battery, wind, diesel | Single | Both | • DT enables real-time monitoring, optimisation, and reliable energy management. • Helps balance demand/supply under stochastic load conditions. • Supports improved efficiency, cost savings and sustainability. | All | Technician, engineer | Distributed EMS decomposed into two levels: • Local controllers (optimise unit cost functions) • Microgrid centralised controller (coordinates overall optimisation) Stochastic loads modeled using probabilistic methods and Markov chains. DT continuously updates with real-time data from MG components. | 1. System Modeling Components • Microgrid Components: The DT models include dispatchable sources (DS), distributed generation (DG, including PVs, wind turbines, diesel generators), and loads (both controllable and stochastic). • Network Topology: Modeled as a radial network with buses and branches represented by electrical parameters such as resistance, reactance, and voltages. • Time Discretisation: The system operates over a discrete-time horizon T={0,1,...,T−1}, with optimisation and control decisions updated at each time step. 2. Modeling Framework • Electrical Models: Power flows based on AC power flow equations, including voltage, active, and reactive power flows with nonlinear constraints. • Load Modeling: Loads are treated as stochastic variables modeled through Markov chains and probabilistic forecasting, capturing real-world uncertainties. • Device Constraints: Battery SOC, charge/discharge rates, inverter capacities, and ramping limits on generation units are explicitly modeled via mathematical constraints. • Cost Functions: Each device (battery, load, generator) is modeled with cost functions reflecting operational costs, switching penalties, and economic terms. 3. Digital Twin Data Flow & Processing • Data Acquisition: Sensor data and forecasting models feed real-time or historical data on generation, load, and network parameters. • Data Management: Utilises data compression and efficient storage to handle large-scale data volumes; communication protocols prioritise critical data, minimising network traffic to accommodate hardware limitations. 4. Optimisation Architecture • Hierarchical Control: - Local Controllers (LCs): Each DER and load manages its own optimisation locally to minimise costs and operational constraints, using the latest local information. - Microgrid Centralised Controller (MGCC): Coordinates global optimisation integrating network constraints, voltage limits, and aggregate power balance. • Iterative Distributed Optimisation: The global cost function is decomposed, and LCs and MGCC iteratively exchange variables such as power setpoints and Lagrange multipliers to converge on optimal operation. • Relaxation of Non-Convex Constraints: Key nonlinear power flow constraints are relaxed to convex forms to allow efficient optimisation. 5. Computation and Algorithm • Moth Flame Optimisation Algorithm (MFOA): A bio-inspired swarm intelligence algorithm used for solving the nonlinear optimisation problem efficiently, avoiding local minima. • Algorithm Loop: - Initialise variables, set control laws. - Each LC solves its own device-level optimisation given control inputs. - MGCC updates global variables considering network constraints and broadcasts updated control signals. - Iterate until convergence criteria met or maximum iterations reached. 6. Real-Time Operation Features • Supports both grid-connected and islanded microgrid modes. • Robust to communication failures modeled with probabilistic failure rates. • Enables dynamic updating of power plans based on evolving forecasts and measurements. • Incorporates droop control and phase-lock loop (PLL) based control schemes for DER frequency and voltage regulation. 7. Physical-Digital Integration • The DT mirrors real asset operation through data feeds, predictive modeling, and feedback-based control. • Forecast errors and uncertainties incorporated via stochastic models. • Enables data-driven operation and planning for MGs to maximise renewable integration and economic benefits. Closed loop: Physical MG assets (DERs, loads, grid) w/ Sensors & data acquisition -> DT model (network + device models + stochastic load) -> Optimisation engine (consists of LCs + MGCC + MFOA) -> Control commands -> Physical assets This architecture allows a balance between computational efficiency, real-time response, and high-fidelity simulation of microgrid operation within the DT framework, enabling optimal energy management under uncertainty. | • Moth Flame Optimisation algorithm (MFOA) -> for solving the energy optimisation problem. • Time homegenous Markov chains -> for generating stochastic load cases. • Droop Control Model: a droop control architecture based on an enhanced phase-locked loop (EPLL), which helps synchronise distributed energy resources (DERs) with load variations and renewable energy fluctuations. | • Inverters and droop control for power sharing and frequency regulation • Phase-Locked Loop (PLL) for synchronisation in grid-connected mode • Sensor network for real-time measurement and communication links with probabilistic failure modeling • Hierarchical EMS structure deployed through Local Controllers (LCs) and MG Central Controller (MGCC) | • Simulated microgrid with PV, wind, diesel and batteries. • Day-ahead planning tested under islanded and grid-connected modes. • Communication failures introduced to test robustness of distributed EMS vs centralised EMS. | • Distributed EMS achieved lower costs compared to centralised EMS. • Maintained bus voltages within limits under stochastic load conditions. • Both grid-connected and islanded modes of the algorithm robust against communication failures. | 1. Uncertainty and stochastic loads - Loads in the microgrid cannot be predicted accurately. - The DT must model loads as stochastic variables using probabilistic and Markov chain approaches to handle uncertainty. - This adds complexity to optimisation and control since inaccurate modeling could lead to poor decisions 2. Complex optimisation problem - The EMS is formulated as a non-convex Optimal Power Flow (OPF) problem, which is computationally hard to solve. - Relaxing constraints to convex forms and applying advanced algorithms (like the Moth Flame Optimisation Algorithm, MFOA) are required, but these bring their own design and convergence challenges 3. Integration of distribution network constraints - Unlike many existing approaches that ignore grid limitations, this study highlights that voltage, ramping, and network constraints must be modeled within the DT. - This increases fidelity but also complicates simulation and optimisation 4. Communication failures - The microgrid depends on communication between local controllers (LCs) and the centralised controller (MGCC). - Failures in the communication network (e.g., packet loss with 0.3 probability in tests) can destabilise centralised EMS. 5. Hardware limitations - DT implementation faces constraints in computational resources, storage capacity, and network bandwidth. - The study notes the need for resource-efficient algorithms, compression techniques, and optimised data exchange protocols 6. Real-time responsiveness - To be useful, the DT must perform real-time optimisation and decision-making. - Balancing real-time operation with accuracy and computational feasibility is a major challenge | • Study validated through simulation only, not real deployment. • Potential hardware constraints: computational resources, storage capacity, bandwidth constraints | • Distributed EMS with DT improves microgrid energy management under uncertainty. • Achieves cost efficiency, robustness and reliability. • Facilitates integration of renewables and transition to sustainable power systems. • MFOA within DT framework proven effective for stochastic optimisation.
Y.3 | A microgrid is a cluster of interconnected Distributed Generations (DGs), loads, and Energy Storage Systems (ESSs) that can operate in grid-connected and islanded modes. | This paper focuses on the design, validation, and implementation of a model-driven microgrid controller using ETAP software. It introduces advanced technologies such as the Model-Driven Approach, Digital Twin Technology, and a Software Development Framework for Power System Applications to address challenges in microgrid management. The ETAP microgrid controller is designed to simplify the development and testing of microgrid control functions, optimise microgrid operations, and facilitate seamless transitions between grid-connected and islanded modes. | Residential & Commercial | BESS RES (wind & solar) Backup generator | Interconnected | Both | The purpose of DT implementation in this case study is centered on the microgrid controller, not the entire microgrid system. 1. Feasibility studies: • The DT enables accurate feasibility studies to determine the optimal size of renewable energy resources, energy storage ratings, and capacity during the planning stage. • This ensures that the microgrid is designed to meet operational and economic objectives effectively. 2. Real-time analysis and testing: • DT provides a virtual representation of the microgrid controller, allowing for real-time analysis and testing of control functions in a simulated environment. • This helps validate the controller's performance before deployment. 3. Optimisation of resources: • By using DT, the microgrid controller can optimise the utilisation of energy resources, minimise operational costs and improve energy efficiency. • It supports functions like economic dispatch, renewable smoothing and reactive power control. 4. Cross-platform functionality: • The DT is hardware-independent and supports virtualised objects/functions that can be executed online within the controller software or offline in the ETAP simulation environment. • This flexibility enhances the controller's adaptability to different hardware and software platforms. 5. Integration with supervisory systems: • DT allows for seamless integration with higher-level supervisory systems such as ADMS, GMS and DERMS, enabling coordinated control and monitoring of the microgrid. 6. Enhanced decision-making: • DT facilitates predictive maintenance and better decision-making by simulating various operational scenarios and evaluating the impact of different control strategies | All | Operator, engineer, maintenance, researcher | 1. Model-Driven Approach -> the microgrid model built in ETAP provides asset data, connectivity and constraints, which are transferred to the controller settings 2. DT Technology -> the controller’s DT mirrors the real controller (identical code runs in both), enabling feasibility studies, validation and optimisation 3. Software Framework for Power System Applications -> a patent-pending ETAP framework that allows fast development and enhancement of new control functions, like an “app store” in smartphones | DT is implemented as part of the controller-in-the-loop simulation: • Digital Twin of Controller: The ETAP microgrid controller DT (identical to the real controller code) runs in ETAP’s simulation environment • Simulation Environment: ETAP provides real-time load flow and transient stability simulations at microgrid scale, with the controller DT interacting with the simulated assets • Communication Setup: TCP/IP-based communication between the simulated microgrid and the DT controller, mimicking real operational conditions Functions Demonstrated: Economic dispatch, renewable smoothing, reactive power control, planned/unplanned islanding, black start, reconnection -> all validated via DT-based controller testing | 1. Simulation & Modeling Platforms • ETAP software -> to design the microgrid, model assets, and simulate system dynamics • ETAP Real-Time Microgrid Simulator (RTMS) -> performs real-time load flow and transient stability analysis at microgrid scale, providing the simulation environment for controller-in-the-loop 2. Optimisation Algorithms -> for economic dispatch, planned islanding and emission/cost trade-offs • Algorithms include load/generation balancing, minimising cost, maximising islanding duration, minimising emissions. 3. Forecasting Tools • ETAP Load Forecasting Manager -> short-term load forecasting using historical demand, weather data (temperature, humidity) and external forecasts • Solar & Wind Forecasting -> based on irradiance, temperature, weather forecasts, and historical generation 4. Communication Infrastructure • TCP/IP-based communication between ETAP simulator and controller for real-time data exchange • Protocol conversion via Gateway (GOOSE messaging, DNP3, HTTPS-based UI) to interact with DERs and higher-level systems 5. Human-Machine Interface • Web-based user interface (HTTPS) -provides operators access to monitoring, dispatching, and configuration | • Rugged controller hardware / Gateway RT controller • Field protocols (DNP3, iCE™, Modbus implied) | 7 scenarios tested: 1. Economic Dispatch - BESS charging when generation > demand (1:00-7:00), discharging at peak demand to reduce grid import 2. Renewable Smoothing - BESS mitigate fast fluctuations of renewable output by rate-limiting active power exchange 3. Reactive Power/Voltage Control - Controller adjusts reactive resources (capacitors, STATCOM, PV inverter, BESS) to follow a scheduled voltage profile 4. Planned Islanding - Controller optimises storage SoC and generator dispatch before disconnecting from grid; sheds some loads as needed 5. Unplanned Islanding - Fault at POI triggers fast transition (within milliseconds) to islanded mode with pre-computed load shedding and BESS switching to grid-forming mode 6. Black Start - If microgrid is fully de-energised, controller starts V/f source (storage or generator) and reconnects loads step-by-step 7. Reconnection - Controller coordinates synchronisation and resynchronisation with the grid | 1. Uncertainty and stochastic loads - Loads in the microgrid cannot be predicted accurately. - The DT must model loads as stochastic variables using probabilistic and Markov chain approaches to handle uncertainty. - This adds complexity to optimisation and control since inaccurate modeling could lead to poor decisions 2. Complex optimisation problem - The EMS is formulated as a non-convex Optimal Power Flow (OPF) problem, which is computationally hard to solve. - Relaxing constraints to convex forms and applying advanced algorithms (like the Moth Flame Optimisation Algorithm, MFOA) are required, but these bring their own design and convergence challenges 3. Integration of distribution network constraints - Unlike many existing approaches that ignore grid limitations, this study highlights that voltage, ramping, and network constraints must be modeled within the DT. - This increases fidelity but also complicates simulation and optimisation 4. Communication failures - The microgrid depends on communication between local controllers (LCs) and the centralised controller (MGCC). - Failures in the communication network (e.g., packet loss with 0.3 probability in tests) can destabilise centralised EMS. 5. Hardware limitations - DT implementation faces constraints in computational resources, storage capacity, and network bandwidth. - The study notes the need for resource-efficient algorithms, compression techniques, and optimised data exchange protocols 6. Real-time responsiveness - To be useful, the DT must perform real-time optimisation and decision-making. - Balancing real-time operation with accuracy and computational feasibility is a major challenge | 1. Complexity in Modeling and Simulation Challenge: Developing an accurate Digital Twin model requires detailed information about the microgrid's assets, connectivity, and operational constraints. Impact: Without precise modeling, the DT may fail to provide reliable feasibility studies or optimal sizing of renewable energy resources and energy storage systems. 2. Hardware Independence Challenge: The DT must be hardware-independent and capable of functioning across different platforms (Linux and Windows). Ensuring compatibility with various hardware configurations can be difficult. Impact: This complexity may limit the DT's adaptability to diverse microgrid setups. 3. Integration with Supervisory Systems Challenge: The DT must interact seamlessly with higher-level supervisory systems such as ADMS, GMS and DERMS. Impact: Ensuring smooth integration and communication between the DT and these systems requires advanced software frameworks and protocols. 4. Real-Time Analysis and Validation Challenge: The DT must perform real-time load flow and transient stability analysis while interacting with protective devices and supervisory controllers. Impact: Achieving real-time performance and validation of control functions can be computationally intensive and time-consuming. 5. Cost and Time for Development Challenge: Developing and enhancing microgrid control functions using the DT can be costly and time-consuming, especially for custom applications. Impact: This may limit the scalability and affordability of DT implementation for smaller or less complex microgrid systems. 6. Dynamic Reconfiguration Challenge: The DT must handle dynamic reconfiguration, such as adding or removing parts of one microgrid to another during fault incidents or operational changes. Impact: Managing such dynamic changes requires advanced algorithms and robust software frameworks. 7. Handling Nested Microgrids Challenge: The DT must manage nested microgrids, where each nested microgrid has its own Point of Interconnection (POI) and operational constraints. Impact: Ensuring proper coordination and control across nested microgrids adds complexity to the DT implementation. | 1. Lack of detailed real-world validation - the paper does not include real-world implementation or field testing of the ETAP microgrid controller 2. Limited discussion on scalability - the paper does not extensively discuss the scalability of the ETAP microgrid controller for larger or more complex microgrid systems, especially those with multiple nested microgrids or high levels of renewable penetration 3. Dependency on ETAP Software - limit accessibility for users who do not have ETAP software or prefer open-source solutions | The case study validates the ETAP microgrid controller as a powerful tool for modern microgrid management, addressing challenges in conventional controllers and enabling advanced functionalities through Digital Twin integration. While the study is primarily simulation-based, it provides a strong foundation for real-world applications and further research into scalable and cost-effective microgrid solutions.
Y.4 | Microgrid … offers localised control over power generation and distribution | The paper addresses the challenges faced by microgrids, which offer localised control and enhanced integration of renewable energy, but require sophisticated real-time monitoring, control and optimisation tools. DT technology is identified as a promising solution that creates a real-time virtual replica of the physical microgrid, enabling advanced energy management without disrupting operations. The study focuses on a real-world multi-energy microgrid at the Singapore Institute of Technology, encompassing interconnected nanogrids with solar PV, diesel generators, battery storage and controllable loads, serving as a practical testbed for developing and validating a cognitive DT that integrates cloud-based optimisation and real-time local control to enhance microgrid efficiency, reliabilitys and sustainability. | Building | BESS, PV, diesel | Interconnected | Both | • creates a virtual replica of a physical system and leverages real-time data, analytics, and optimisation algorithms to enable advanced monitoring, control and optimisation. • For microgrids, DTs allow efficient energy management and seamless integration of renewable sources by simulating various operation and response scenarios, without disrupting the actual grid. • Thus, DTs can improve the decision making and reliability in decentralised microgrids with optimised scheduling and control. | All | Researcher, operator, manager | Multilayer architecture including: • Physical microgrid: buildings, PV, DG, BESS, loads. • DT Client: located near physical assets, uses OPC UA for real-time data exchange and control. • DT Server: cloud-hosted, runs computation-heavy optimisation and learning algorithms. | Communication Protocols: • Between the physical microgrid and DT Client, OPC Unified Architecture (UA) protocol is used for real-time, bidirectional, standardised data exchange. • Between the DT Client and the DT Server, socket programming (TCP/IP) enables robust and low-latency data transmission of microgrid state data and control actions. Data Flow: • Microgrid states (e.g., battery state of charge, PV generation, load demand, electricity prices) are continuously collected and updated in the OPC UA server. • The DT Client polls these states regularly (e.g., every 15 minutes) and then sends them via sockets to the DT Server. • The DT Server runs optimisation and ML algorithms on these input states to compute optimal control actions. • Generated control actions are communicated back to the DT Client, which writes them to the OPC UA server. • Physical components read these action commands from the OPC UA server to adjust operation accordingly. Algorithmic Implementation: • The DT Server implements a real-time optimisation algorithm for power scheduling via a fast, one-step mixed-integer linear programming. • A hybrid algorithm combining imitation learning and deep neural networks controls battery charge/discharge policies. • This design avoids heavy discretisation, enabling fast training and inference compared to standard reinforcement learning. System Testing: • The DT system is tested in Matlab/Simulink simulations reflecting real microgrid configurations. • Communication and control data exchange demonstrations validate low latency and real-time synchronisation. | • OPC Unified Architecture (UA) for industrial-grade, scalable, cross-platform communication. • Socket programming for efficient, low-latency cloud communication.Machine learning: imitation learning and neural networks for control policy. • Matlab/Simulink for microgrid simulation and integration testing. • Cloud infrastructure enabling scalable deployment and flexible algorithm execution. | • Generation & Storage : PV arrays with MPPT; diesel generator; BESS (600 kWh, inverter-based) • Power Electronics : IGBT bridge converters, PWM control, PLL for grid sync • Sensors & Measurement : Smart meters, PMUs, current/voltage/SoC sensors • Control & Communication : Relays, RTUs, local controllers | Real-world microgrid at Singapore’s SIT campus, covering: Two interconnected nanogrids (buildings W3 and W5) with local and centralised BESS. Components include solar PV, diesel generators, and variable loads. A 24-hour operation simulation highlighting: • Battery charging/discharging based on demand and solar generation. • Power exchange between nanogrids and main grid. • Response to unexpected events such as circuit breaker opening and islanding. • Validation of DT's ability to manage energy flow and optimise operational cost under realistic conditions. | • DT achieved operation cost within 0.24% of the theoretical optimal, outperforming MPC, Q-learning and PPO algorithms. • Demonstrates fast computation and low-latency communication suitable for real-time control. • DT maintained smooth transitions between grid-connected and islanded modes. • Case studies showed effective battery scheduling, power balancing and event handling. | • Maintaining real-time synchronisation between physical and cyber systems due to communication latencies. • Handling dynamic nature and uncertainties in microgrid operation. • Ensuring robust communication, especially during network disturbances. • Balancing the computational load between cloud and edge to meet latency requirements. | • Implementation study limited to a specific university microgrid setup; generalisability to other types remains to be validated. • Assumes reliable communication infrastructure; less exploration of highly unstable network conditions. • Latency considerations ideal for current setup; may require enhancements for faster or larger scale systems. • Future work needed to integrate more diverse components like (EVs) and other DERs. | • Developed a cognitive Digital Twin integrating physical microgrid, DT client and cloud server with advanced communication and optimisation. • Demonstrated that the DT can achieve near-optimal energy management, supporting grid resilience and sustainability. • DT is scalable and adaptable to various microgrid configurations due to modular design and flexible algorithms. • The study paves the way for broader DT adoption in smart grids and highlights future directions such as expanding component integration and incorporating risk mitigation.
Y.5 | N/A | This paper focuses on a digital twin (DT) model-based approach to optimise energy costs in residential community microgrids. The study is conducted using a single-phase residential microgrid platform called SMARTNESS, located at the National School of Engineering, Tunis. The use case demonstrates how the DT framework validates the microgrid's operation and how the proposed EMS reduces electricity costs for the community. | 4 prosumers | PV, BESS | interconnected | Both | 1. Replication and validation of the real microgrid platform The DT was developed to replicate the operation of the SMARTNESS microgrid platform installed at ENIT (National School of Engineering, Tunis). It aimed to mirror the behavior, operation, and performance of the real system using MATLAB/Simulink, including PV generation, loads, battery storage, and energy flows The DT was validated against real-world measurements, with an error rate of <2% between DT predictions and physical platform data 2. Testing & optimising energy management The DT served as a safe environment for testing a new cost optimisation strategy for peer-to-peer (P2P) energy trading within the community microgrid. It enabled predictive analysis and scenario testing (e.g., sunny vs. cloudy days, different load profiles) to determine how optimised battery usage by a single prosumer could reduce costs for the entire community Using the DT, they demonstrated that optimised EMS reduced the community’s electricity bill by turning a 4900 millimes/day cost into a 3040 millimes/day profit | All | EMS developer, researcher | Conceptual framework revolves around the use of a DT to optimise energy costs and enhance the efficiency of residential community microgrids. It includes the following key elements: 1. DT design: - Replicates the functionality of the physical microgrid platform. - Incorporates predictive analysis and optimisation algorithms. - Excludes real-time monitoring in its initial stage. 2. Energy Management System (EMS): - Aims to optimise energy costs for prosumers in the community. - Incorporates P2P energy trading and centralised decision-making. - Focuses on two distinct prosumer behaviors: those with PV systems but no storage and a single prosumer with a storage system. 3. Cost optimisation: - Uses linear programming (LP) to minimise electricity costs for the community. - Regulates battery usage to align with energy price profiles and maximise community profit. 4. Validation: - Ensures the accuracy of the DT framework by comparing simulation results with real-world data. - Maintains a predefined error rate of less than 2%. | Communication Protocols: • Between the physical microgrid and DT Client, OPC Unified Architecture (UA) protocol is used for real-time, bidirectional, standardised data exchange. • Between the DT Client and the DT Server, socket programming (TCP/IP) enables robust and low-latency data transmission of microgrid state data and control actions. Data Flow: • Microgrid states (e.g., battery state of charge, PV generation, load demand, electricity prices) are continuously collected and updated in the OPC UA server. • The DT Client polls these states regularly (e.g., every 15 minutes) and then sends them via sockets to the DT Server. • The DT Server runs optimisation and ML algorithms on these input states to compute optimal control actions. • Generated control actions are communicated back to the DT Client, which writes them to the OPC UA server. • Physical components read these action commands from the OPC UA server to adjust operation accordingly. Algorithmic Implementation: • The DT Server implements a real-time optimisation algorithm for power scheduling via a fast, one-step mixed-integer linear programming. • A hybrid algorithm combining imitation learning and deep neural networks controls battery charge/discharge policies. • This design avoids heavy discretisation, enabling fast training and inference compared to standard reinforcement learning. System Testing: • The DT system is tested in Matlab/Simulink simulations reflecting real microgrid configurations. • Communication and control data exchange demonstrations validate low latency and real-time synchronisation. | MATLAB/Simulink - for modeling and simulation of the microgrid components and EMS Optimisation solver: Linear Programming (LP) - algorithm to minimise community electricity cost | SMARTNESS microgrid platform consisting of PV arrays, 48 V batteries, local and central EMS units, and smart meters interconnected via an AC single-phase bus to the grid. | • Context: A residential community microgrid in a lab setting (SMARTNESS platform, ENIT, Tunis). The microgrid has 4 prosumers, each with PV systems; 1 prosumer has a battery, and the central unit also has storage • Scenario: The authors investigate P2P energy trading where: - 3 prosumers use PV-only (no storage) to meet their own loads, injecting surplus into the community microgrid. - 1 prosumer with storage actively exchanges energy, optimising battery usage to reduce costs for the entire community • Tests performed: - Experimental data collection: from the SMARTNESS platform under different load/PV conditions (sunny vs. cloudy days, multiple load profiles). - DT replication: MATLAB/Simulink model calibrated with real data. - Optimisation applied: Linear Programming (LP) EMS strategy tested in the DT environment to minimise community energy cost. • Validation: - Compared DT outputs vs. physical platform results (SOC error <2%). - Showed that cost optimisation with the new EMS reduced daily bill from 4900 millimes (loss) → 3040 millimes (profit) | Communication Protocols: • Between the physical microgrid and DT Client, OPC Unified Architecture (UA) protocol is used for real-time, bidirectional, standardised data exchange. • Between the DT Client and the DT Server, socket programming (TCP/IP) enables robust and low-latency data transmission of microgrid state data and control actions. Data Flow: • Microgrid states (e.g., battery state of charge, PV generation, load demand, electricity prices) are continuously collected and updated in the OPC UA server. • The DT Client polls these states regularly (e.g., every 15 minutes) and then sends them via sockets to the DT Server. • The DT Server runs optimisation and ML algorithms on these input states to compute optimal control actions. • Generated control actions are communicated back to the DT Client, which writes them to the OPC UA server. • Physical components read these action commands from the OPC UA server to adjust operation accordingly. Algorithmic Implementation: • The DT Server implements a real-time optimisation algorithm for power scheduling via a fast, one-step mixed-integer linear programming. • A hybrid algorithm combining imitation learning and deep neural networks controls battery charge/discharge policies. • This design avoids heavy discretisation, enabling fast training and inference compared to standard reinforcement learning. System Testing: • The DT system is tested in Matlab/Simulink simulations reflecting real microgrid configurations. • Communication and control data exchange demonstrations validate low latency and real-time synchronisation. | • Calibration & Validation - The EMS of the real platform was treated as a black box, so the DT had to be built from observation and reverse-engineering. - Required extensive testing (sunny vs. cloudy, different load profiles) to achieve error <2% • Battery Modeling & Constraints - The DT had to respect SOC limits, charge/discharge constraints, and PV curtailment protocols from the manufacturer, which made optimisation more complex. | 1. No real-time synchronisation - The DT does not exchange data with the physical microgrid in real time 2. Single-prosumer optimisation - The proposed EMS optimisation focuses on one prosumer with storage, while other prosumers are PV-only. - A full community-level EMS (with a coordinator or multi-agent approach) is not implemented yet. 3. Laboratory scale - The study is limited to a small lab-scale microgrid (4 prosumers, ~12.9 kWp PV). - Scalability to larger or real-world residential communities is not demonstrated. 4. Simplified data use - Load demand (Pload) was not predicted in the DT stage - they used internally designed load profiles for tests, not residential consumption datasets 5. Single optimisation algorithm - They only tested linear programming (LP) for cost optimisation. - Future work aims to compare against other optimisation methods (e.g., genetic algorithms) | The DT successfully replicated the physical microgrid platform and enabled safe testing of EMS optimisation strategies. The optimised EMS demonstrated significant cost savings for the community, showing that DTs can be a powerful tool for designing and validating P2P microgrid energy trading strategies.
Y.6 | N/A | The paper is grounded in the broader energy transition toward smart grids and distributed renewable generation, particularly solar photovoltaic (PV) systems in residential contexts. Key motivations include: • Rising Energy demand has increased production costs for utilities, making demand response (DR) essential to balance supply and demand. • The Integration of renewable energy sources (mainly PV) introduces stochasticity and uncertainty, complicating load scheduling and cost optimisation. • Smart information and communication technologies (ICT) now enable decentralised and automated energy management at the household or microgrid level. • Digital Twin (DT) concepts offer a way to mirror and manage physical energy systems in real time, while Reinforcement Learning (RL) provides adaptive decision-making under uncertainty. | Residential | PV | single | grid-connected | Digital Twin layers represent: 1. Smart home loads and local PV generation 2. Aggregated data at neighborhood transformer 3. Central control for tariff optimisation this allows bidirectional data flow (measurement ↔ control) between the physical devices and the digital model. | no predictive | Energy Operators | The study proposes a multi-layer Digital Twin conceptual framework for smart residential microgrids, in which Reinforcement Learning (RL) functions as the intelligent decision-making core that continuously optimises load scheduling under uncertain PV generation and dynamic electricity pricing. The DT mirrors each physical component household units, neighborhood transformer, and grid interface. Enables bidirectional information exchange through a hierarchical communication structure. This framework integrates data modeling, decision-learning, and cyber-physical synchronisation to achieve cost-effective and user-centric energy management. | • Physical System Data Acquisition: Smart home sensors and intelligent appliance meters (IAMs) gather real-time data on load profiles and PV generation. • Digital Twin Modeling: Each household’s DT replicates appliance behaviors, energy consumption patterns, and user comfort parameters such as the unit delay cost (udc), appliance priority (Pₕ), and nominal power (Nₐ). • Learning and Optimisation: A Reinforcement Learning (RL) agent (specifically Q-learning) embedded within the DT determines optimal scheduling actions-ON/OFF decisions and grid/PV power allocation-to minimise total electricity cost while satisfying operational constraints. • Control and Actuation: The DT dispatches optimised control commands to physical devices through the communication layer. • Feedback and Update: The DT continuously updates its internal state using real-time sensor feedback and new tariff information, thereby maintaining synchronisation between the physical microgrid and its virtual model. This closed-loop interaction between the physical system and its digital counterpart forms the core operational logic of the proposed Digital Twin framework. | • IoT sensing and edge computing for smart home DTs • Cloud platforms for neighborhood and central control DTs • Reinforcement Learning frameworks (Python,MATLAB) for decision optimisation • Secure communication and data analytics tools for interopability and feedback control | • Smart inverters / converters for DC-AC conversion and grid coupling. • Voltage & frequency control (fixed grid-connected mode). • Smart meters • Local automation modules for ON/OFF switching based on DT commands. | Simulated residential on-grid microgrid equipped with a rooftop PV system, smart appliances, and time-of-use tariffs. The Digital Twin framework mirrors the home’s energy system and employs a Reinforcement Learning agent to optimise load scheduling under uncertainty of solar power and variable energy pricing. This scenario demonstrates that the DT-RL framework can effectively prescribe cost-minimising, user-aware load schedules. validating the theoretical claim. | • Energy cost: RL scheduling reduced daily energy cost versus unscheduled operation; the paper shows modest savings in the no-PV test and qualitative gains with PV (no 90% figure reported). • Runtime: RL converged ~1.5-2× faster than the baseline optimisation method (LA) in the reported experiment. • User comfort: The udc parameter effectively models delay-discomfort and its cost impact. • Comparison: RL achieved similar or better cost vs the LA baseline while being faster; no GWOA comparison is presented. • Validation: The DT-RL system adaptively prescribed cost-efficient, user-aware load schedules under uncertain PV and dynamic tariffs in simulation. | Anticipated for deployment: • Real-time data & comms: Maintaining low-latency, secure, bidirectional flows between physical devices and the DT; lag or loss would degrade RL control quality. • Edge resources: Running RL/DT logic at home gateways may face CPU/RAM constraints. | • Simulation-only evaluation (no HIL/field tests). • Simplified appliance-user behavior (priority windows, udc). • Energy sources limited to PV + grid; no storage/EV. • No real-time comms implementation or experimental validation. • Scalability and interoperability not empirically evaluated. | A multi-layer DT with Q-learning in simulation is able to prescribe cost-efficient, user-aware schedules for residential, grid-connected microgrids with PV and dynamic tariffs. Integrating storage, adding real-time comms, and performing HIL/field validation are the next steps toward comprehensive microgrid control.
Y.7 | Microgrids (MGs) are defined by the United States Dept. of Energy to be a set of interlinked loads and distributed power sources inside precisely outlined limits, acting as one controllable unit on the grids which are able to be operated in either islanded mode or non-islanding mode. | The paper proposes a Digital Twin-based Energy Management System (DT-EMS) for a microgrid that integrates multiple distributed generation units and storage devices. The DT framework mirrors the physical microgrid in real time and enables dynamic monitoring, scheduling, and control to optimise performance under varying operating conditions. | Residential | Micro-turbine, Wind Turbine, PV, ESS | interconnected | both | The Digital Twin serves as a cyber-physical intelligence layer that replicates the microgrid’s physical assets and operational dynamics in real time. It supports system monitoring, optimisation, prediction, and validation, while also enabling accurate ESS management, fault detection, and scenario-based simulation. By integrating with the optimisation algorithm, the DT provides decision-support and adaptive control, ensuring efficient, resilient, and scalable operation of urban microgrids under both islanded and grid-connected conditions. | All | Operator, engineer, researcher and system designer | Structured into three layers: 1. Physical Layer : represent the real microgrid. 2. Information Interaction Layer : the data communication and synchronisation layer that enables real-time data exchange between the physical microgrid and its virtual twin. 3. Application Layer : the virtual twin of the microgrid that performs data processing, prediction, and optimisation. It hosts the energy management algorithms, decision rules and visualisation functions. | The implementation is a simulation-based DT-EMS : • Architecture Type : A three-layer digital twin architecture ( physical -> information -> application). • Simulation Platform : The DT model and optimisation were implemented in a simulation environment (e.g., MATLAB/Simulink) • Communication Interface • Optimisation Module : The EMS employs hybrid optimisation algorithms to minimise operational cost and improve system stability under both grid-connected and islanded modes. • Synchronisation Mechanism : continuously updating the virtual model using measured data, and sending optimisation results or control actions bact to the physical system • Experiment Scenario : Test the framework under different operation modes and generation condiftions to evaluate economic and stability performance improvements compared to conventional control. | • Improved Pigeon-Inspired Optimisation Algorithm (IPIOA): Main algorithm for energy scheduling, dispatch optimisation, and cost minimisation. | Energy Management System (EMS) • Controls DER dispatch under both islanded and grid-connected modes. • Incorporates time-of-use (TOU) pricing, ramp-rate, and capacity constraints. | 1. 24-hour DT-assisted unit commitment / economic dispatch (UC/ED) of a low-voltage urban microgrid under time-of-use (TOU) pricing. 2. Two operating modes evaluated: grid-connected (with tie-line exchange) and islanded. 3. Resources modeled: micro-turbines, wind turbines, photovoltaic generation, and energy storage systems (ESS). 4. Objective: minimise operating cost subject to system constraints, including load balance, generator limits, minimum up/down times and ramps, ESS limits, and tie-line limits. 5. Method: Digital Twin used for device/system modeling and scenario analysis; optimisation solved with the Improved Pigeon-Inspired Optimisation Algorithm (IPIOA). | 1. The DT supports the EMS by enabling accurate device/system modeling, prediction (e.g., ESS behavior), and scenario-based optimisation/decision support. It is presented as simulation-based (not demonstrated as real-time streaming). 2. The IPIOA-based DT-EMS shows improved economic performance and robustness versus existing methods in the case studies, supporting the feasibility and advantage of DT-assisted microgrid energy management. | 1. Scalability of the DT (models and hardware) for larger or more complex microgrids is critical and non-trivial. 2. Accurate multi-DER and ESS modeling and coordination under TOU in both grid-connected and islanded modes raises fidelity and constraint-handling demands. 3. Real-time data synchronisation and communication architecture are not specified; deploying a streaming DT would require robust, low-latency data exchange and timing guarantees. | 1. Simulation-only evaluation; no HIL or field validation is presented. 2. Communication architecture and real-time synchronisation are not specified; interoperability is therefore unverified. 3. Evaluated on an urban low-voltage microgrid; scalability/generalisability to larger or more complex systems is not established. 4. Optimisation results are shown via case studies with IPIOA; broader parameter sensitivity and cross-case tuning are not reported. 5. Forecast uncertainty is not analysed; the study does not evaluate the impact of RES/load forecast errors on decisions. | This study demonstrates that a Digital Twin-assisted EMS coupled with the Improved Pigeon-Inspired Optimisation Algorithm achieves superior economic and robust operation for urban microgrids under TOU in both grid-connected and islanded modes, establishing feasibility while highlighting the need for real-world validation and scalable DT architectures beyond simulation.
Y.8 | • DER (Distributed Energy Resource) : the renewable and distributed generation units inside a microgrid, specifically solar photovoltaic (PV) panels, wind turbines, and battery energy storage systems (BESS). • MG (Microgrid) : a local power system unit capable of operating both grid-connected and islanded, integrating DERs and energy storage through intelligent control. • SG (Smart grid) : advanced power-system evolutions that integrate “a growing number of devices” and require larger-area control and sensor network management. | The study addresses the growing complexity of renewable-rich, distributed energy systems. It proposes, implements, and experimentally validates a Digital Twin Microgrid (DTMG) framework that 1. Digitally replicates a microgrid comprising photovoltaic, wind, and battery energy storage systems using data-driven models. 2. Optimises real-time power generation through machine-learning-based and gradient-descent optimisation algorithms. 3. Applies self-healing control to autonomously detect and respond to component faults or performance degradation. | Laboratory | PV, Wind Turbine, BESS | single | both | 1. Real-time, bidirectional synchronisation -The DT runs as a cloud-hosted layer that continuously exchanges sensor states and control actions with the lab microgrid (“digital model → digital shadow → intelligent DT layer”), enabling closed-loop control. 2. Optimisation with computational-efficiency awareness -The objective explicitly balances renewable generation with a computation-cost term Cc(t), reflecting the paper’s aim to be real-time and lightweight. 3. Model-based self-healing -Health-state detection and actuation are formalised and realised with a logistic-regression classifier that triggers recovery actions when faults/performance degradations are detected. 4. Safety & sustainability constraints baked into control -The DT enforces battery SoC dynamics/limits and power-balance constraints while minimising imbalance ΔP, supporting safe islanded/grid-connected operation with minimal human intervention. | All | Operator, Researcher, grid designer | Multi-layer, bidirectional Digital Twin-Microgrid (DT-MG) architecture • The framework is explicitly described as multi-layer and hierarchical, consisting of the physical microgrid layer, sensor/instrumentation layer, cloud/communication layer, and the digital-twin layer. • The paper states that “the physical and twin layers are maintained in bidirectional communication”, confirming that real-time data flow occurs both from the physical system to the DT (data acquisition, monitoring) and from the DT back to the physical system (control and actuation). • Within this structure, information passes upward through sensors and cloud interfaces, while optimised control commands and self-healing actions propagate downward to the physical assets. • This multi-layer, bidirectional design enables continuous synchronisation between the physical microgrid (PV, WT, BESS) and its digital representation, ensuring that both operate as one integrated cyber-physical system. | Multi-layer bidirectional DT-MG integration: 1. Physical Grid Layer -The real lab microgrid consisting of PV, wind turbine, and BESS. 2. Sensor & Instrumentation Layer -Data acquisition via voltage, current, temperature, irradiance, and wind sensors feeding to the DT. 3. Communication/Cloud Layer -Wi-Fi / TCP-IP link enabling real-time synchronisation, data storage, and historical retrieval. 4. Digital Twin Layer -Cloud-hosted hybrid models (physics+data) and control logic (digital model → digital shadow → intelligent DT). 5. Interface / HMI Layer -Visualisation dashboard for monitoring and supervisory control. | • Cloud-hosted DT (digital model → shadow → intelligent layer) • Real-time sync via Wi-Fi/TCP-IP (bidirectional) • Polynomial regression for PV/WT/BESS models • Gradient-descent optimisation (real-time dispatch) • Logistic-regression self-healing (fault detection/action) • Cloud database (real-time + historical) • Web dashboard (monitoring/HMI) | • Charge controller, inverter/converters, load interface • Sensors: voltage, current, temperature, irradiance, wind speed/direction • DAQ + dSPACE controller (real-time control) • IoT/Wi-Fi gateway (DT link) • Grid tie & islanding switch/relays (mode control) | A regression-based Digital Twin Microgrid (DTMG) was implemented and validated in real time on a lab PV-WT-BESS microgrid, combining polynomial-regression component models, gradient-descent optimisation, and a logistic-regression self-healing module. It maintained bidirectional digital-physical synchronisation via a cloud/communication stack and demonstrated classifier-driven health-state detection with corrective actuation, while explicitly accounting for computational cost to keep control practical in real time. | • The digital twin framework achieved the desired synchronisation between the physical and digital microgrids. • The data-driven modeling (polynomial regression) captured PV/WT/BESS dynamics with computationally lightweight execution, practical for real-time control. • The self-healing function validated classifier-based autonomous fault management (detection and actuation). • Although results were shown on a laboratory microgrid, the architecture is proposed as scalable to large-scale distributed systems. | • Modeling complexity: Balancing fidelity vs. computational efficiency in PV/WT/BESS models; the objective explicitly includes a computation-cost term to keep models/controllers lightweight. • Real-time performance: Maintaining bidirectional, real-time DT↔MG synchronisation while running optimisation and control concurrently; complexity increases as the framework scales to multiple MGs. • Data quality dependence: Data-driven models’ accuracy hinges on the quality/coverage of sensor data and operating ranges. • Communication & interoperability: Larger deployments will need robust, standardised industrial protocols to integrate heterogeneous devices/controllers and ensure reliable cloud/edge links. (Implied by the multi-layer DT/communication stack; avoid naming specific cloud vendors.) • Uncertainty & nonlinearity: Fast irradiance/wind changes challenge regression models and may degrade accuracy; handle with robust features and update schemes. • End-to-end integration: Orchestrating sensors, DAQ, controllers, Wi-Fi, cloud DB, and ML into one synchronised pipeline introduces heterogeneity in timing/sampling and architecture. | 1. Not universal out-of-the-box: Models are tuned to the lab MG; applying to different MG topologies/components requires re-modeling/re-tuning. 2. Scale & reliability not yet field-validated: Results are lab-scale; large-scale, distributed deployments remain proposed. 3. Lifecycle/model drift: Accuracy can decline as components age; the paper’s data-driven approach suggests periodic re-training, but lifecycle strategies aren’t detailed. | • A regression-based DT framework (polynomial regression + gradient descent + logistic-regression self-healing) can model, optimise, and self-heal MG operations in real time with explicit attention to computational cost. • Laboratory validation demonstrates technical feasibility and indicates scalability potential toward interconnected MGs. • The framework provides a basis for DT-enabled smart-grid applications; future work should address universality across MG variants, lifecycle/drift management, standardised communications, and field-scale validation.
Y.9 | N/A | the Deakin Microgrid Digital Twin (DMDT) - a web-based software platform designed to: Provide operators with AI-driven insights and real-time data visualisation, Enable power generation prediction, health monitoring, anomaly detection, and energy management simulation. A key part of the study is comparing different machine learning (ML) and deep learning models for predicting solar power generation using real data from Deakin’s on-site weather and power sensors. The prediction capability is vital for DT applications such as performance evaluation, load balancing, and predictive maintenance. | Campus | PV, BESS | single | grid-connected | The main purpose of the Digital Twin in this study is to act as an AI-driven operational and research platform that enhances the monitoring, prediction, and management of Deakin University’s renewable microgrid. Its core function is accurate, real-time solar power generation prediction, which supports performance evaluation, decision-making, optimisation, and fault or anomaly detection, effectively bridging the physical solar farm with its digital analytical environment. | Descriptive, Predictive | Operator, Researcher | N/A | The DT platform is web-based, developed in-house at Deakin University. • It uses real-time sensor and weather station data from the Deakin solar farm. • Machine learning models (SVR, LS-SVR, RF, XGBoost, ANN, CNN, LSTM) were implemented and compared for solar power prediction. • The best-performing model (Random Forest) was integrated into the operational DMDT for real-time prediction. • The DT also supports 2D/3D visualisation, health monitoring, anomaly detection, and data simulation. • Users (operators and researchers) interact via a web interface for monitoring and analytics. | Predictive models: • Support Vector Regression (SVR) • Least Squares SVR (LS-SVR) • Random Forest (RF) • XGBoost • Artificial Neural Network (ANN) • Convolutional Neural Network (CNN) • Long Short-Term Memory (LSTM) | Control and monitoring infrastructure: -Microgrid PLC Controller: AZZO M580 HSBY (Programmable Logic Controller for supervisory control and redundancy) -Solar Plant Controllers: SMA Power Plant Controller and SMA Inverter Manager (central coordination and grid compliance) -Inverters: • Three central inverters -SMA Sunny Central 2500-EV • Four string inverters -SMA STP60 -Tracking System: NextTracker Controller Units for solar array orientation control | The study focuses on a real-world campus-scale application of the Deakin Renewable Energy Microgrid, leveraging operational data from the solar farm and on-site sensors to develop, compare, and deploy AI-based solar power prediction models within the Deakin Microgrid Digital Twin (DMDT) framework. The scenario demonstrates how the DMDT supports real-time monitoring, performance evaluation, and predictive energy management through data-driven analytics. | • Among seven AI models trained on real Deakin Microgrid data (SVR, LS-SVR, RF, XGBoost, ANN, CNN, LSTM), ANN achieved the highest point-accuracy (R² ≈ 0.944 with the lowest RMSE) but had much longer training time (≈144 s), limiting practicality. • Using the paper’s two novel robustness metrics-the x-percentile Closeness and x-percentile Absolute Error spectra-Random Forest delivered the smallest absolute relative error across the spectrum, very fast training (~4.9 s; XGBoost ~5.1 s), and sub-second prediction, so it was selected for real-time deployment in the Deakin Microgrid Digital Twin (DMDT). • Overall, the study shows that a DT powered by ML-based predictive analytics can accurately forecast solar generation and support operational decision-making for a campus-scale, grid-connected renewable microgrid. | • Field data quality: The study notes inconsistencies and anomalies in weather and power data and explicitly performs error detection on the weather-power pairs; this underscores a dependency on noisy field sensors (weather station, inverter telemetry) and environmental variability. • Compute burden for deep models: ANN/CNN/LSTM incur significantly longer training times than tree-based methods, which constrains online/near-real-time DT use; inference is sub-second, but training cost is non-trivial for frequent model refresh. | • Narrow data window: Results are based on ~one month of summer operation (e.g., late Dec-late Jan), so the training set spans a limited range of irradiance/meteorology and load patterns. • Scope of DT functions: The implemented DT capabilities are descriptive (visualisation/monitoring) and predictive (power forecasting; anomaly triggers). Prescriptive/control/self-optimising functions are not in scope in this paper. • Deep model practicality: Deep nets train much slower (e.g., ANN ~144 s vs RF ~4.9 s; XGBoost ~5.1 s), which limits their practicality for frequent retraining or low-latency MLOps within the DT. | AI-based predictive analytics within a microgrid digital twin can materially improve real-time decision support and situational awareness. Across seven tested models, Random Forest offered the best balance of accuracy, robustness (via percentile-based error spectra), and computational efficiency, and was therefore selected for real-time deployment in the Deakin Microgrid Digital Twin.
Y.10 | N/A | The rapid growth of distributed renewable energy resources (especially residential PV), which are increasingly connected to local microgrids or smart-home energy systems. While this decentralisation supports sustainability and resilience, it also creates challenges for real-time energy management - the fluctuating nature of solar generation and varying household loads require fast coordination that traditional centralised control can’t provide. Digital Twin as a virtual representation of each physical microgrid (or smart-home energy node), synchronised through the fog computing as the enabling layer between end devices and cloud services. Unlike purely cloud-based control, fog nodes can perform local computation, data filtering, and control decisions close to the energy sources and appliances. | Residential | PV, WT | interconnected | grid-connected | The Digital Twin aims to provide real-time, intelligent management and optimisation for renewable-based residential microgrids by virtually replicating their physical operation. It leverages a fog computing layer as the intermediary between local devices and cloud services, enabling low-latency data synchronisation, local decision-making, and coordinated energy sharing among interconnected smart homes. | All | EMS Operators, Researcher | 1. Physical layer: Smart-home microgrids (PV/WT) and the grid-the sources of measurements and the targets of control. 2. Fog/edge layer: A community fog server that aggregates data, coordinates surplus-power sharing, and hosts/executes DT decision logic (ANN forecasts + MGWO optimisation). 3. Cloud layer: Referenced conceptually for scalability and storage in the fog-vs-cloud discussion. | 1. Layer: Physical Components: PV, wind turbine, household loads, smart meters; connection to commercial grid Responsibilities: Provide real-time measurements; receive control set-points; consume/export energy 2. Layer: Fog / Edge Components: Community fog server / local gateway; DT decision logic (ANN + MGWO); local datastore Responsibilities: Aggregate data; forecast PV/WT; optimise dispatch and imports (ToU aware); push set-points; enable peer-to-peer energy sharing 3. Layer: Cloud Components: Centralised storage/analytics platform (not concretely implemented) Responsibilities: Long-term data retention, historical analysis, potential backup computation; fog prioritised for low latency | • IoT Communication Protocol • Fog / Edge Computing Platform • Predictive model : artificial neural network (ANN) and modified grey wolf optimiser (MGWO) | • Smart meters for measurement and bidirectional communication. | A simulation-based case study of a residential smart-home microgrid cluster (each home with PV and wind, household loads, smart meters) connected to a fog server and the utility grid. The DT integrates ANN forecasting and MGWO optimisation to coordinate local energy sharing and minimise cost/imports under ToU pricing. | The fog-enabled DT framework, combining ANN forecasting with MGWO optimisation, reduced community energy cost and grid imports in simulation for residential smart-home microgrids coordinated via a fog server. The paper motivates fog (vs. pure cloud) for lower latency conceptually, but does not report a measured cloud-only vs fog benchmark. | • Real-time synchronisation and coordination among distributed smart-home microgrids. • Handling renewable generation uncertainty and load variability. • Ensuring convergence and scalability of the MGWO-based optimisation. • Maintaining reliable data communication and interoperability between IoT layers. • Undefined computational split between fog and cloud layers. | • Simulation-based validation only; no hardware or real-time testing. • Fog vs. cloud performance not empirically compared. • Communication, sensor reliability, and cybersecurity untested. • DER set limited to PV and wind (no storage/EV). • Computational role split between fog and cloud not specified. • Scalability and robustness not evaluated for larger networks. | The study demonstrates a fog-enabled Digital Twin framework integrating ANN-based forecasting and MGWO-based optimisation for cost-effective operation of residential smart-home microgrids. Through simulation, the framework validates the feasibility of using fog computing for decentralised energy management and optimisation, conceptually supporting real-time coordination and reduced grid dependency. It's recommended to extend the framework to real-world implementation to evaluate performance under practical communication and control conditions.
Y.11 | N/A | Proposes integrating Digital Twin (DT) and Reinforcement Learning (RL) for microgrid energy management. The DT acts as a virtual replica of the physical microgrid, allowing real-time simulation and learning of optimal control decisions under uncertain wind and solar conditions. The RL framework continuously improves battery scheduling to minimise cost and balance renewable generation and demand | Laboratory | WT, PV, BESS | single | grid-connected | • Real-time DT replication (simulation) of a single, grid-connected MG (WT, PVs, BESS). • Host RL-based EMS (two-steps-ahead battery scheduling) for cost minimisation. • Model stochastic generation/load to support adaptive, uncertainty-aware decision-making. • Serve as a lab-scale testbed for optimisation, sensitivity analysis, and conceptual validation (no HIL). | All | Researcher | 1. Physical Microgrid Layer: Single grid-connected MG with a local user, one wind turbine, five PV units, and a battery linked to the external grid via a transformer. 2. Digital Twin Layer: Real-time simulation model of that MG used to study and learn energy-management policies (lab/simulation setting, not field HIL). 3. Reinforcement Learning Layer: Q-learning with two-steps-ahead look-ahead operating inside the DT to prescribe battery scheduling that minimises cost under uncertain renewable conditions. 4. Decision & Feedback Layer: Actions computed by RL are evaluated in the DT; the paper validates in simulation and positions this as a research testbed. | Implementation components include: 1. Modeling tools • Wind: Markov-chain model with 6 operating wind-speed states plus failure/repair dynamics; failures more likely at high wind. • Load: Top-down statistical demand profile (hour/day/week peaks). • Battery: Discrete-time state tracking of charge/discharge flows. • PV: Forecasted availability is used. 2. Algorithm (Q-learning, two-step look-ahead) • Initialise Q; predict next two steps (wind via MCM, load via profile, PV via forecast). • Evaluate charge/discharge decisions, compute cost-based reward with discounting, and update Q until convergence; include sensitivity tests on learning variables. 3. Simulation setup • Hourly time step; fixed price and simplified physical losses/limits to keep learning tractable; lab-scale DT validation only (no live dispatch). • Single, grid-connected MG with local user, WT, 5×PV, and a battery linked to the external grid via transformer; wind transition/repair tables as above. | • Reinforcement Learning (Q-learning, two-step look-ahead) for battery scheduling and cost minimisation. • Markov Chain modeling for stochastic wind states plus failure/repair dynamics. • Optimisation via a multi-criteria reward (cost focus, with design to boost peak-time battery use and local • Statistical load profiling and DT simulation environment (lab-scale) to validate the RL policy. | • Power interface: transformer for grid connection and bidirectional power exchange. • Local controller/EMS logic: controls charging, discharging, and import/export decisions according to RL recommendations. • Measurement and communication: implied monitoring of power, load, and cost data for DT synchronisation. | A simulation-based experimental study of a single-user, renewable-based microgrid operating under uncertain wind and solar conditions. 1. Two key simulation cases were created for sensitivity testing : • Case 1: Low wind power output (WPO) + high load demand. • Case 2: High wind power output + low load demand. Each case starts with an initial battery charge of 3000 Wh and runs through multiple decision sequences for learning 2. The reinforcement learning model explores combinations of: • Weight coefficient (k) → defines preference for charging vs discharging. • Discount factor (γ) → defines emphasis on future rewards. • Learning rate (α) → controls convergence speed. 3. The simulation analyses how different parameter settings affect the algorithm’s ability to reach optimal scheduling under uncertainty | • The DT-RL architecture successfully learned optimal battery scheduling for different environmental conditions. • The trained agent balanced charging (during high renewable output) and discharging (during high demand) to minimise the total energy cost. • The system dynamically adapted to stochastic wind and solar variations and produced stable convergence of Q-values (meaning the algorithm “learned” an optimal policy). | • High fluctuation in wind/PV makes RL prediction complex • Continuous DT learning loop increases processing time | • Physical simplification : ignores losses, battery aging and line limits • Model designed for one user and one MG node | Integrating a Digital Twin with reinforcement learning provides an effective, adaptive, and data-driven approach for real-time energy optimisation in renewable microgrids. The model successfully demonstrates the feasibility of smart, self-learning microgrid management, though future research should focus on scaling, hardware validation, and integration with larger grid environments.
Y.12 | N/A | The growing need for sustainable and reliable energy systems in remote or islanded areas where grid connection is unavailable or unstable. Traditional fossil-fuel-based systems are inefficient and environmentally harmful, so hybrid microgrids (HMGs) integrating renewable energy resources (RERs) (such as photovoltaic (PV) solar and biogas generation) and energy storage systems (notably Vanadium Redox Flow Battery Systems (VRFBS)) are seen as a viable solution. While hybrid microgrids are promising, their complex energy flow and dynamic resource availability require advanced control and monitoring frameworks . | Laboratory, Residential, Island communities | PV, Biogas Generator, BESS (Vanadium Redox Flow Battery Systems) | single | both | It is designed to mirror, monitor, and optimise the performance of the Smart Islanded Hybrid Microgrid (HMG) in real time that : 1. Synchronises physical and simulated data from renewable and storage components. 2. Enables intelligent energy management. 3. Improves monitoring, control, and performance optimisation of the islanded system. | Descriptive | Operator, Engineer, Researcher | 1. Physical Layer (Real System) : Contains physical components of the Smart Islanded Hybrid Microgrid (HMG) that connected via an AC bus, enabling energy exchange between generation, storage and loads. 2. Cyber Layer (Digital Twin Model) : Represents a virtual replica of the HMG that runs simulations and reflects real-time operational states by receiving live data from sensors and control devices through IoT communication that is used for visualisation and performance analysis. 3. Communication Layer (IoT Middleware) : Integrates the physical and virtual systems using Raspberry Pi, MODBUS, and MQTT protocols that handles real-time synchronisation and data transmission between field devices and the cloud. 4. Cloud / Control Layer : Cloud dashboard for data monitoring, visualisation, and manual control adjustments. | 1. System modeling and simulation: Model PV, biogas, and VRFBS subsystems. Simulate power balance and SOC dynamics 2. IoT integration : Deploy sensors and Raspberry Pi to collect real-time voltage/current data then communicate via MODBUS and MATT. 3. Data transmission and cloud connection : send operational data to a cloud server for monitoring and storage 4. Dashboard Visualisaton : Display live data and system status through a web-based interface. 5. Validation and performance testing : Compare simulated results (DT model) with actual physical readings from the hybrid microgrid. | 1. IoT controller : Raspberry Pi 2. Communication protocol : MODBUS and MATT (Message Alignment Telemetry Transference) 3. Data Handling : Real-time telemetry via MATT | 1. Measurement & Control : Sensors + Raspberry Pi controller, LabView enabled smart controller 2. Interconnection : AC bus | The scenario involves developing and testing a Smart Islanded Hybrid Microgrid composed of PV, biogas, and VRFBS units connected via an AC bus. A Raspberry Pi controller uses MODBUS and MATT (Message Alignment Telemetry Transference) protocols to send real-time data to a cloud dashboard, forming the Digital Twin. The scenario demonstrates successful real-time monitoring, communication, and visualisation of the microgrid’s operation, validating the DT’s role as a real-time mirror of the physical system. | The results section demonstrates that the Smart Islanded Hybrid Microgrid (HMG) prototype and its Digital Twin successfully achieved: 1. Stable power supply through coordinated operation of PV, biogas, and VRFBS 2. Reliable data communication between devices via MODBUS and MATT 3. Accurate real-time data visualisation on the cloud dashboard. These outcomes confirm that the DT framework can mirror the physical system’s behavior effectively. The findings confirm the technical feasibility of using a DT for small-scale, islanded microgrid management and provide a foundation for future work in intelligent optimisation and predictive analytics. | N/A | • The DT-HMG system is demonstrated as a single microgrid instance, monitored by a single user interface. | The IoT-enabled ICS + EMP consistently met the selected community’s dynamic load by strategically scheduling RERs, VRFBS, and the grid (when available); during daytime grid outages, loads were maintained by optimising the BGP generator as the primary AC supply, while PV kept operating via its grid-tied inverter against a dummy AC grid formed by the BGP reference bus-assuring continuous supply and stronger energy security/DSM. A cost comparison further showed the RP-enabled controller is markedly more economical than a LabVIEW-based controller.

## Deployment context
Paper | Deployment context
| Building | Residential | Commercial | Lab/simulation
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Building | Single-facility deployment
| Residential | Interconnected smart homes/neighbourhood
| Commercial | Enterprise-scale, revenue-bearing operations (across multiple assets/buildings)
| Lab/simulation | Cyber-physical testbed/simulation

## DER composition
Paper | DER Composition
| Solar PV | EV | Battery | Wind | Diesel | Biogas Generator
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Solar PV | Converts solar irradiance into electrical energy
| EV | Acts as both a flexible load and mobile storage unit
| Battery | Provides short-term energy storage and frequency regulation
| Wind | Generates variable power through wind turbines
| Diesel | Supplies dispatchable backup power for islanded or emergency operation
| Biogas | Produces renewable, controllable generation from organic waste

## Topology
Paper | Grid Topology
| Single microgrid | Multi microgrid
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Single microgrid | a stand-alone microgrid operating independently or connected to a single utility grid, focusing on internal coordination of local DERs and loads.
| Multi microgrid | an interconnected network of multiple microgrids that exchange power and coordinate control strategies across local and global layers.

## Operating mode
Paper | Mode
| Islanded | Grid-connected
2
3
11
Y.1
Y.3
Y.2
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Islanded | operates independently from the main utility grid, relying solely on its local generation, storage and control resources to maintain stability and balance.
| Grid-connected | operates in coordination with the main utility grid, allowing energy exchange and external support for reliability, economic optimisation or ancillary services

## Purpose
Paper | Purpose
| System representation & validation | Real-time monitoring & synchronisation | Predictive analysis & forecasting | Optimisation & control | Operational decision support | Maintenance guidance | Simulation & experimental validation | Design & planning support | Integration & interoperability enablement
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| System representation & validation | DT built to replicate, emulate, or validate the physical microgrid, EMS, or controller.
| Real-time monitoring & synchronisation | Continuous, bidirectional data flow for monitoring device states and maintaining cyber-physical synchronisation.
| Predictive analysis & forecasting | Use of analytical or AI/ML models for forecasting and predictive insights.
| Optimisation & control | Optimisation of operation, dispatch or cost using EMS algorithms, RL or multi-objective functions.
| Operational decision support | DT is used to enhance operator or system decision-making during operation (not design stage)
| Maintenance guidance | DT assists in predictive or opportunistic maintenance decisions
| Simulation & experimental validation | DT acts as a sandbox for testing, what-if analysis, or algorithmic experimentation without risking real assets.
| Design & planning support | DT used for feasibility studies, resource sizing and early-stage planning.
| Integration & interoperability enablement | DT facilitates communication, hardware independence or integration across systems and platforms.

## User
Paper | User
| System operators | Maintenance & field technicians | Managers & decision makers | Designers & developers | Researchers & academics
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Representative Users | Role/Interaction
| System Operators | Operator, Energy Operator, EMS Operator, Building Operator | Operate & control the microgrid
| Maintenance & Field Technicians | Technician, O&M Operator | Maintain & troubleshoot assets
| Managers & Decision Makers | Manager, DSO, Policymaker | Plan, evaluate and decide strategies
| Designers & Developers | Engineer, System/EMS/ecoMG Developer | Build, design and integrate DT/EMS systems
| Researchers & Academics | Researcher, Academic Engineer | Explore, test and validate DT concepts

## Data analytics type
Paper | Data Analytics Type
| Descriptive | Predictive | Prescriptive
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6 |  |  |  | no predictive despite having prescriptive, because RL agent prescribes schedules directly from the DT state and tariffs
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Descriptive | Summarises and visualises historical data to explain what happened and identify patterns or trends.
| Predictive | Uses statistical and machine-learning models on historical data to estimate what is likely to happen next
| Prescriptive | Recommends specific actions by optimising against objectives and constraints, often using simulation or optimisation to suggest what to do.

## Implementation Framework
Paper | Implementation framework
| Layered/modular architecture | Real-time physical-digital synchronisation | Hybrid modeling: physics + data-driven | Hierarchical & distributed control | Closed-loop control & feedback | Standardised communication & data models | Simulation-based scenario testing | Agent-Based Simulation (ABS) modeling | High fidelity EMT modelling | Hardware-in-the-Loop (HIL) integration | Optimisation-integrated EMS
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Layered/modular architecture | Structural design of the DT framework, separating functional layers (physical, data, model, service, application)
| Real-time physical-digital synchronisation | Ensures continuous bidirectional data flow between physical microgrid and its DT counterpart.
| Hybrid modeling: physics + data-driven | Combines physical (equation-based) and data-driven (ML/AI) models within DT.
| Hierarchical & distributed control | Multi-level or multi-agent control strategy coordinating local and global layers.
| Closed-loop control & feedback | DT participates in real-time decision loops that feed control actions back to physical system.
| Standardised communication & data models | Use of interoperable protocols (e.g., MQTT, IEC 61850, OPC UA) or standardised data schemas.
| Simulation-based scenario testing | Virtual experimentation and what-if scenario evaluation in a simulated DT environment.
| Agent-Based Simulation (ABS) modeling | DT implemented through agent-based modeling (multi-entity behavioral simulation).
| High fidelity EMT modelling | Detailed electrical modeling at electromagnetic-transient (EMT) timescales.
| Hardware-in-the-Loop (HIL) integration | Real-time coupling between DT simulation and physical components (controllers, devices).
| Optimisation-integrated EMS | Embeds optimisation algorithms (e.g., MILP, RL, GA) within DT-based EMS for decision-making.

## Technology-microgrid side
Paper | Technology-microgrid side
| Power conversion & grid interconnection equipment | Sensors & measurement infrastructure | Control systems hardware | Communication & networking technologies | Energy management & optimisation systems | Experimental testbed infrastructure
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Power conversion & grid interconnection equipment | Includes inverters, converters, transformers, filters, circuit breakers, PLL, droop control.
Examples: DC/DC and DC/AC converters, PLL, IGBT bridge converters, PWM control, smart inverters, circuit breakers, grid coupling interface.
| Sensors & Measurement Infrastructure | Covers all sensing, metering, and monitoring equipment for current, voltage, power, SoC, environmental variables, etc.
Examples: Smart meters, PMUs, current/voltage/temperature sensors, irradiance/wind sensors, power and cost monitoring.
| Control systems hardware | Includes controllers, PLCs, RTUs, RTACs, local/central EMS logic, gateways, and embedded control units.
Examples: Siemens MGC A8050, RTAC, AZZO M580 PLC, local controllers, EMS, rugged controllers, Raspberry Pi, dSPACE controller.
| Communication & networking technologies | Includes protocols, network infrastructure, and IoT gateways enabling data exchange between MG and DT layers.
Examples: IEC 60870-5-104, MQTT, Modbus TCP, DNP3, iCE™, fiber optic networks, IoT/Wi-Fi gateways, communication links with failure modeling.
| Energy management & optimisation systems | Refers to high-level supervisory or intelligent energy management systems responsible for optimisation, scheduling and coordination.
Examples: ecoMG tool with MPC, Intelligent Energy Management (IEM), EMS modules, TOU optimisation, central EMS, SMA Power Plant Controller.
| Experimental testbed infrastructure | Used for experimental or testbed setups enabling data collection, synchronisation and simulation coupling.
Examples: OPAL-RT RT-Lab, dSPACE controller, DAQ systems, LabView smart controller.

## Technology-DT side
Paper | Technology-DT side
| Virtual modelling environments | Cyber-physical synchronisation system | Optimisation & control algorithms | Predictive modeling & forecasting techniques | Fault diagnosis & reliability modeling | Communication & integration middleware | Visualisation & HMI systems | Cloud, edge & IoT infrastructure | Data processing & conversion services
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag | Detail
| Virtual modelling environments | Covers all simulation environments and modeling frameworks used to emulate microgrid behavior (static, dynamic, or real-time).
examples : OPAL-RT RT-Lab, AnyLogic (ABS), RTDS (RSCAD), ETAP RTMS, MATLAB/Simulink, cloud-based simulation layers
| Cyber-physical synchronisation system | Includes real-time, hardware-in-the-loop (HIL), or cyber-physical synchronisation setups enabling DT-MG coupling.
examples : RTDS + NovaCor core, ETAP controller-in-the-loop, Wi-Fi/TCP-IP real-time sync, IoT Raspberry Pi with Modbus/MATT telemetry.
| Optimisation & control algorithms | Algorithms for cost minimisation, scheduling, dispatch optimisation, control policy learning, or resource allocation.
examples: Gurobi solver, LP optimisation, MFOa, IPIOA, reinforcement learning (Q-learning, imitation learning), gradient descent, multi-criteria reward control.
| Predictive modeling & forecasting techniques | Data-driven models for forecasting load, generation, or faults; includes regression and ML-based predictors.
examples: LSTM, SVR, RF, XGBoost, ANN, CNN, Markov chains, polynomial regression, statistical load profiling, forecasting modules.
| Fault diagnosis & reliability modeling | Techniques and frameworks used for reliability analysis, fault propagation, and opportunistic maintenance planning.
examples: Fault Tree Analysis (FTA), reliability/failure Markov modeling, risk importance metrics, self-healing via logistic regression.
| Communication & integration middleware | Communication protocols, middleware layers, and software used for DT-MG data exchange and system interoperability.
examples: MQTT-Modbus conversion, TCP/IP, OPC UA, GOOSE messaging, DNP3, cloud communication sockets, interoperability tools.
| Visualisation & HMI systems | Interfaces for operator interaction, monitoring dashboards, and real-time visualisation.
examples: SCADA HMI, web dashboards, HTTPS-based operator UI, visualisation of system state.
| Cloud, edge & IoT infrastructure | Distributed computing or data-management components supporting DT deployment, synchronisation, or scalability.
examples: Cloud/edge layers for control, fog computing, IoT sensing, cloud database hosting, telemetry data pipelines.
| Data processing & conversion services | Software layers handling data translation, acquisition, or storage between DT and MG components.
examples: Data Acquisition Service (MQTT-to-Modbus), telemetry via MATT, gateway protocol conversion modules

## Challenge
Paper | Challenge
| Real-time synchronisation & latency | Data quality & sensor reliability | Modeling complexity & fidelity trade-offs | Protocol heterogeneity & interoperability | Expensive computational cost | Stochastic uncertainty | Communication reliability | Hardware/resource constraints | HIL/CIL deployment complexity | Scalability and integration to larger/multi-MG systems | Calibration & validation effort | Dynamic reconfiguration & nested microgrids
2
3
11
Y.1
Y.2
Y.3
Y.4
Y.5
Y.6
Y.7
Y.8
Y.9
Y.10
Y.11
Y.12
*attribute covered in the paper
| Tag |  |  |  | Detail
| Real-time synchronisation & latency |  |  |  | Ensuring bidirectional data and control exchange between the physical and digital systems with minimal delay; maintaining time alignment for effective feedback and decision-making.
| Data quality & sensor reliability |  |  |  | Dependence on accurate, continuous, and noise-free field measurements; challenges due to faulty sensors, missing data, or environmental variability affecting model fidelity.
| Modeling complexity & fidelity trade-offs |  |  |  | Balancing detailed physical and control models with computational feasibility; overly simplified models reduce realism, while high-fidelity models increase cost and execution time.
| Protocol heterogeneity & interoperability |  |  |  | Integrating devices, controllers, and DT components using different communication protocols or standards (e.g., MQTT, Modbus, OPC UA); ensuring seamless data translation and system compatibility.
| Expensive computational cost |  |  |  | High processing demand of optimisation algorithms, forecasting models, or AI training; trade-off between algorithmic accuracy, convergence time, and real-time usability.
| Stochastic uncertainty |  |  |  | Handling randomness and variability in renewable generation, demand profiles, or component failures through probabilistic or stochastic models.
| Communication reliability |  |  |  | Maintaining dependable and secure information exchange; addressing packet loss, latency spikes, or link failures that degrade DT performance and control accuracy.
| Hardware/resource constraints |  |  |  | Limited memory, or network capacity in edge, IoT, or embedded devices used for DT deployment; impacts scalability and model complexity.
| HIL/CIL deployment complexity |  |  |  | Engineering and synchronisation challenges in setting up hardware- or controller-in-the-loop experiments to validate DTs in real time.
| Scalability to larger/multi-MG systems |  |  |  | Extending DT frameworks to multiple interconnected microgrids or larger systems while maintaining accuracy, coordination, and manageable computation.
| Calibration & validation effort |  |  |  | Extensive testing, parameter tuning, and data comparison required to align DT outputs with real-world behavior; often time-consuming and iterative.
| Dynamic reconfiguration & nested microgrids |  |  |  | Managing reconfiguration events such as faults, grid disconnections, or multi-microgrid interactions where topology and control boundaries change dynamically.